SECTION 16530

UTILITY FLOOR BOXES

PART 1 – GENERAL

  - SCOPE

The contractor, as part of the work of this section, shall coordinate, receive, connect and place into operation all equipment.  The contractor shall furnish all conduit, wire, connector, hardware, pipe, fittings, and other incidental items necessary for the completion and functioning electrical outputs as described herein and shown on the plans.

The contractor shall coordinate the mounting of the utility boxes among all associated trades.

The Contractor shall provide complete assembly for electrical power, telephone data, air, water and drain, in a concrete-tight, non-corrosive enclosure suitable for flush floor installation in high vehicular traffic areas with very high concentrated loads.

  - MANUFACTURER’S SERVICES

- The manufacturer shall submit shop drawings for approval within 30 days after receipt of a purchase order.  No fabrication of equipment is to proceed prior to approval of these drawings.

- One manufacturer shall be responsible for the complete product (floor box).

C.  Upon completion, manufacturer shall provide documentation consisting of operating and maintenance instructions, engineering test reports, drawings, and spare parts list.

  - QUALITY ASSURANCE

- Manufacturer’s products shall be listed by Underwriters Laboratories, Inc. (UL) if a Standard for the finished product described herein exists. If no UL Standard exists for the finished product described herein, manufacturer shall certify that the complete specified product was fabricated in accordance with quality standards set forth in UL Standard 714 in a facility routinely subjected to UL field inspections.

- Equipment specified herein shall be the standard product of a single manufacturer with a minimum of 10 years experience manufacturing Utility Floor Boxes.  The boxes shall be manufactured by Maxicom 1100 W. Indiana Avenue Philadelphia, PA 19133 215.225.2200.

- Manufacturer shall supply testing documentation required by the specifying engineer.

  - WARRANTY

All equipment shall be warranted free of defects in materials and workmanship for a period of eighteen (18) months from the date of shipment, or one (1) year from the date of installation, whichever occurs first.

PART 2 - PRODUCT

2.01	MANUFACTURER'S REQUIREMENTS

A. The equipment herein specified is

- EXH 2222 DH 		(22" X 22" frame size, double single hinge access door).

- EXH 2222 DL 		(22" X 22" frame size, double lift-out access door).

- EXH 2727 DH 		(27" X 27" frame size, double single hinge access door*).

- EXH 2727 DL 		(27" X 27" frame size, double lift-out access door*).

- EXH 2727 QH 		(27" X 27" frame size, quadruple single hinge access door*).

- EXH 2727 QL 		(27" X 27" frame size, quadruple lift-out access door*).

- EXH 2234 DH 		(22" X 34" frame size, double single hinge access door*).

- EXH 2234 DL 		(22 "X 34" frame size, double lift-out access door*).

* with 5" beam for operable wall).

as manufactured by Maxicom 1100 W. Indiana Avenue Philadelphia, PA 19133 215.225.2200 and shall serve to indicate the quality of equipment required.  Base bid shall be for the equipment by MAXICOM.  If alternate equipment is proposed, it shall be shown as an addition to or deduction from the base bid price and shall be subject to approval.

B.	Other manufacturers who wish to bid must submit a complete bill of materials, company information, and certified test results listing qualifications to the Architect ten (10) days prior to bid.  Bid approval signed by the Architect must be supplied at the time of bid.  All manufacturers must comply with the bid specifications.  Exceptions will not be permitted and are grounds for immediate rejection.

2.02	PRODUCT PERFORMANCE

The frame and cover assembly shall withstand the weight of any wheel of a regularly available lift truck having a load capacity of 33,000 pounds, with a maximum total front axle load of 62,500 pounds. For the purpose of this specification the reference lift truck shall be a Caterpillar DP-150 (http://www.cat-lift.com/4-1-2.cfm).

  - PRODUCT CONSTRUCTION

The product ("floor box") supplied shall include the following components:

A.  TRIM FRAME:

1. The trim frame shall be fabricated from .187" steel with a corrosion resistant coating or from .187" stainless steel.

2. The trim frame shall be flush and level with the finished floor.

3. The trim frame shall be securely integrated with the enclosure.

B.  ENCLOSURE:

1.  Product enclosure shall be fabricated from PVC, galvanized steel, or stainless steel.

2.  Partitions shall be welded in place.

3.  Openings in product enclosure shall be cut in the field by others.

C.  LEVELING TABS:

1. Tabs shall be provided to level and secure the trim frame and enclosure assembly during concrete pour.

- COVER ASSEMBLY:

The cover assembly shall include access doors and support frame.

1. Access Doors:

a.  Access doors shall be cast aluminum.

b.  Finish shall be as cast with a non-skid pattern.

c.  Access doors shall mount flush with steel trim frame and floor.

d.  Mating surfaces shall be gasketed.

e.  Aluminum castings shall be of sufficient strength and cross section to comply with aforementioned performance specification.

f.  Access doors must be able to be fully closed even when devices have been plugged-in.

2. Support Frame:

a. Support frame shall be fabricated from cast aluminum.

b. Support frame shall mount flush with steel trim frame and floor.

c. Finish shall be as cast and match with mating access doors.

d. Aluminum castings shall be of sufficient strength and cross section to comply with aforementioned performance specification.

E. DEVICE PLATES:

1. Device plate sub-panel for electrical components shall be fabricated from 300 series stainless steel.

2. Device plates shall be held in place by stainless steel hardware.

3. All devices shall be furnished with gasketed covers.

F.  ASSEMBLY:

1.  Finished assembly of trim, frame and covers are to be flat and level with the floor within 1/8".

2.  Sub-panels fasteners shall be stainless steel.

3. Gaskets shall be 1/8" thick neoprene and resistant to oil, acids, and abrasives. Gaskets to be held in place with adhesive.

2.04	DEVICES PROVIDED

| Device | Description | Manufacturer Product Code | Quantity |
| --- | --- | --- | --- |
| Electrical |  |  |  |
| Receptacles |  |  |  |
| Power Distribution Blocks |  |  |  |
| Breakers |  |  |  |
| Telecommunications |  |  |  |
| Device |  |  |  |
| Device |  |  |  |
| Mechanical |  |  |  |
| Device |  |  |  |
| Device |  |  |  |

2.05	ELECTRICAL DEVICE SPECIFCATIONS (DEFAULT)

A.  DEVICES:

1.  Electrical components shall be UL listed or recognized.

2.  Sub-panels shall be pre-wired prior to shipping.

3.  Minimum 10,000 AIC, RMS.

4.  Lugs rated minimum 75  C.

B.  WIRING:

1.  Wiring shall be 75  C THWN or XHHW.

2.   Color code:

a.  Ground - Green

b.  Neutral - White or gray

c.  A phase - Black

d.  B phase - Red

e.  C phase - Blue

C.  BREAKERS:

1.  30A, 3 pole, 240 VAC molded case, panel mount, reversible lugs and weather resistant cover.

2.  20A, 3 pole, 240 VAC molded case, panel mount, reversible lugs, and weather resistant cover.

3.  20A, 1 pole, 120 VAC molded case, panel mount, reversible lugs, and weather resistant cover.

D.  RECEPTACLES:

1. 100A, 208Y/120V, 5-wire, load make, load break, dead front mount, weather resistant cover.

2.  30A, 208Y/120V, 5-wire, locking panel mount, NEMA L21-30R, with cover.

3.  20A, 208Y/120V, 5-wire, locking panel mount, NEMA L21-20R, with cover.

4.  20A, 125V, GFI, duplex grounding, 3-wire panel mount, heavy duty, NEMA 5-20R, color to match NEMA L21-20R and NEMA L21-30R, with covers.

E.  POWER DISTRIBUTION BLOCKS:

1.  600V rated.

2.  One piece electrical continuity for phases.

3. 75  C.

4.  Single barrel primary entry, size up to AWG #2/0.

5.  Six barrel secondary entry, size AWG #14 to #4.

2.06	TELECOMMUNICATIONS DEVICE SPECIFICATIONS (DEFAULT)

A.  DEVICES:

1.  Category 5e, triplex, RJR-45 connectors.

2.  Type SC, simplex connector, multi-mode fiber optic.

3.  Voice grade RJ-11 connectors.

B.  WIRING:

1.  Wiring by others.

2.07    MECHANICAL DEVICE SPECIFICATIONS (DEFAULT)

A.  QUICK CONNECTS:

1.  Female, 1/2".

2.  Industrial Interchange Series B.

3.  Normally closed.

B.  VALVES:

1.  Ball.

2.  ½ " ID.

3.  200 psig, WOG.

C.  REGULATOR:

1.  ½" NPT.

2.  0 to 125 psig.

3.  Maximum supply pressure 300 psig.

4.  ¼ " gauge port and gauge.

E.  DRAIN:

1.  3" PVC, domed strainer for main drain.

2.  1- ¼ " stainless steel, flat strainer for auxiliaries.

PART 3 - EXECUTION

3.01	INSTALLATION:

Competent parties from several trades are required to coordinate the installation.  Manufacturer shall have no responsibility for design and installation of electrical, low voltage and wet systems beyond the limits of the box supplied. Care must be taken not to damage the box or associated conduit and piping systems. Contractor shall supply temporary covers for use during construction if required.  Installation requirements by the manufacturer shall be adhered to insure overall function and operation of the floor boxes.